## Notes
Notes
Annual results from the Modelica/Dymola cold-storage model, full TMY3 year, Dassl solver, tolerance 1e-6.
Chiller COP and capacity from COP_vs_ambient_sweeps.xlsx, -30 to 50 C ambient, 17 points, linear interpolation.
Part load: COP_full = COP_part / 0.9675, then PLF = 1 - 0.13 (1 - PLR) at the operating part-load ratio.
Capacity scales with Q_box_kW relative to its value at 35 C ambient.
Sheet Annual_21C_limit: hot-side condensing temperature limited to at least 21 C.
Sheet Annual_No_limit: no lower limit on the condensing temperature.
Electricity is chiller compressor electricity only; condenser fans and defrost are not included.
Compare cases within each city; cooling delivered is identical across cases within 0.01%.

## Annual_21C_limit
City | Cycle | Refrigerant | Annual chiller electricity (kWh/yr) | Annual cooling delivered (kWh/yr) | Seasonal COP (cooling / electricity) | Change vs single-stage R134a, same city (%) | Cascade vs single-stage, same refrigerant and city (%) | Max room temperature (C) | Max part-load ratio
Chicago, IL | Single stage | R134a | 85142 | 235061 | 2.761 | 0 |  | -19.19 | 0.776
Chicago, IL | Cascade (with CO2) | R134a | 86932 | 235071 | 2.704 | 2.1 | 2.1 | -19.2 | 0.776
Chicago, IL | Single stage | R1234yf | 87954 | 235058 | 2.672 | 3.3 |  | -19.19 | 0.776
Chicago, IL | Cascade (with CO2) | R1234yf | 88047 | 235069 | 2.67 | 3.41 | 0.11 | -19.2 | 0.776
Chicago, IL | Single stage | R515B | 85887 | 235059 | 2.737 | 0.88 |  | -19.19 | 0.776
Chicago, IL | Cascade (with CO2) | R515B | 86995 | 235070 | 2.702 | 2.18 | 1.29 | -19.2 | 0.776
Atlanta, GA | Single stage | R134a | 90983 | 235062 | 2.584 | 0 |  | -19.19 | 0.788
Atlanta, GA | Cascade (with CO2) | R134a | 92200 | 235070 | 2.55 | 1.34 | 1.34 | -19.2 | 0.781
Atlanta, GA | Single stage | R1234yf | 94447 | 235059 | 2.489 | 3.81 |  | -19.19 | 0.791
Atlanta, GA | Cascade (with CO2) | R1234yf | 93553 | 235069 | 2.513 | 2.82 | -0.95 | -19.2 | 0.782
Atlanta, GA | Single stage | R515B | 91956 | 235060 | 2.556 | 1.07 |  | -19.19 | 0.789
Atlanta, GA | Cascade (with CO2) | R515B | 92317 | 235070 | 2.546 | 1.47 | 0.39 | -19.2 | 0.782
San Diego, CA | Single stage | R134a | 86246 | 235060 | 2.725 | 0 |  | -19.18 | 0.774
San Diego, CA | Cascade (with CO2) | R134a | 88001 | 235069 | 2.671 | 2.03 | 2.03 | -19.19 | 0.772
San Diego, CA | Single stage | R1234yf | 89071 | 235057 | 2.639 | 3.28 |  | -19.18 | 0.777
San Diego, CA | Cascade (with CO2) | R1234yf | 89127 | 235068 | 2.637 | 3.34 | 0.06 | -19.19 | 0.772
San Diego, CA | Single stage | R515B | 86985 | 235058 | 2.702 | 0.86 |  | -19.18 | 0.775
San Diego, CA | Cascade (with CO2) | R515B | 88061 | 235069 | 2.669 | 2.1 | 1.24 | -19.19 | 0.772
Tucson, AZ | Single stage | R134a | 99382 | 235065 | 2.365 | 0 |  | -19.18 | 0.822
Tucson, AZ | Cascade (with CO2) | R134a | 99608 | 235071 | 2.36 | 0.23 | 0.23 | -19.19 | 0.792
Tucson, AZ | Single stage | R1234yf | 104026 | 235063 | 2.26 | 4.67 |  | -19.18 | 0.838
Tucson, AZ | Cascade (with CO2) | R1234yf | 101367 | 235071 | 2.319 | 2 | -2.56 | -19.19 | 0.796
Tucson, AZ | Single stage | R515B | 100776 | 235064 | 2.333 | 1.4 |  | -19.18 | 0.829
Tucson, AZ | Cascade (with CO2) | R515B | 99821 | 235071 | 2.355 | 0.44 | -0.95 | -19.19 | 0.794

## Annual_No_limit
City | Cycle | Refrigerant | Annual chiller electricity (kWh/yr) | Annual cooling delivered (kWh/yr) | Seasonal COP (cooling / electricity) | Change vs single-stage R134a, same city (%) | Cascade vs single-stage, same refrigerant and city (%) | Max room temperature (C) | Max part-load ratio
Chicago, IL | Single stage | R134a | 74481 | 235058 | 3.156 | 0 |  | -19.19 | 0.776
Chicago, IL | Cascade (with CO2) | R134a | 76834 | 235068 | 3.059 | 3.16 | 3.16 | -19.2 | 0.776
Chicago, IL | Single stage | R1234yf | 76752 | 235055 | 3.063 | 3.05 |  | -19.19 | 0.776
Chicago, IL | Cascade (with CO2) | R1234yf | 77721 | 235066 | 3.024 | 4.35 | 1.26 | -19.2 | 0.776
Chicago, IL | Single stage | R515B | 75083 | 235056 | 3.131 | 0.81 |  | -19.19 | 0.776
Chicago, IL | Cascade (with CO2) | R515B | 76867 | 235067 | 3.058 | 3.2 | 2.38 | -19.2 | 0.776
Atlanta, GA | Single stage | R134a | 87164 | 235061 | 2.697 | 0 |  | -19.19 | 0.788
Atlanta, GA | Cascade (with CO2) | R134a | 88620 | 235069 | 2.653 | 1.67 | 1.67 | -19.2 | 0.781
Atlanta, GA | Single stage | R1234yf | 90414 | 235058 | 2.6 | 3.73 |  | -19.19 | 0.791
Atlanta, GA | Cascade (with CO2) | R1234yf | 89881 | 235068 | 2.615 | 3.12 | -0.59 | -19.2 | 0.782
Atlanta, GA | Single stage | R515B | 88083 | 235059 | 2.669 | 1.05 |  | -19.19 | 0.789
Atlanta, GA | Cascade (with CO2) | R515B | 88723 | 235069 | 2.649 | 1.79 | 0.73 | -19.2 | 0.782
San Diego, CA | Single stage | R134a | 85014 | 235060 | 2.765 | 0 |  | -19.18 | 0.774
San Diego, CA | Cascade (with CO2) | R134a | 86865 | 235069 | 2.706 | 2.18 | 2.18 | -19.19 | 0.772
San Diego, CA | Single stage | R1234yf | 87763 | 235056 | 2.678 | 3.23 |  | -19.18 | 0.777
San Diego, CA | Cascade (with CO2) | R1234yf | 87958 | 235068 | 2.673 | 3.46 | 0.22 | -19.19 | 0.772
San Diego, CA | Single stage | R515B | 85737 | 235058 | 2.742 | 0.85 |  | -19.18 | 0.775
San Diego, CA | Cascade (with CO2) | R515B | 86920 | 235069 | 2.704 | 2.24 | 1.38 | -19.19 | 0.772
Tucson, AZ | Single stage | R134a | 98132 | 235065 | 2.395 | 0 |  | -19.18 | 0.822
Tucson, AZ | Cascade (with CO2) | R134a | 98449 | 235071 | 2.388 | 0.32 | 0.32 | -19.19 | 0.792
Tucson, AZ | Single stage | R1234yf | 102701 | 235063 | 2.289 | 4.66 |  | -19.18 | 0.838
Tucson, AZ | Cascade (with CO2) | R1234yf | 100175 | 235070 | 2.347 | 2.08 | -2.46 | -19.19 | 0.796
Tucson, AZ | Single stage | R515B | 99509 | 235064 | 2.362 | 1.4 |  | -19.18 | 0.829
Tucson, AZ | Cascade (with CO2) | R515B | 98656 | 235071 | 2.383 | 0.53 | -0.86 | -19.19 | 0.794

## Cooling_load
Item | Value | Unit | Note
Design cooling capacity | 60 | kW | Rated chiller capacity at 35 C ambient
Room setpoint | -20 | C | Held by PI control of the chiller part-load ratio
Location of the freezer | - | - | Inside a conditioned supermarket at 20 C; condenser outdoors on the roof
Annual cooling load, envelope | 144,191 | kWh/yr | 61% of total; walls and roof face 20 C store air, floor faces 10 C ground
Annual cooling load, product | 84,444 | kWh/yr | 36% of total; daily schedule below
Annual cooling load, door infiltration | 6,982 | kWh/yr | 3% of total; door open 2 min each hour, 08:00-17:00, every day
Annual cooling load, total | 235,617 | kWh/yr | Same in all four cities because the freezer sits inside the 20 C store
Room size | 30 x 25 x 8 | m | Floor 750 m2, volume 6000 m3
U-values wall / roof / floor | 0.18 / 0.15 / 0.25 | W/m2K
Stored product mass | 300 | t
Product load schedule, every day | 0 / 20 / 30 / 25 / 15 / 20 / 5 / 0 | kW | Points at 0 / 8 / 9 / 10 / 12 / 14 / 18 / 22 h, smooth spline between points, repeats daily

## Weather
City | Weather file (tab-delimited TXT) | Hours | Mean dry-bulb (C) | Min (C) | Max (C) | Hours > 20 C | Hours > 30 C
Chicago, IL | Weather_TMY3_Chicago_IL_725300.txt | 8760 | 10 | -22.8 | 35 | 2004 | 148
Atlanta, GA | Weather_TMY3_Atlanta_GA_722190.txt | 8760 | 16.7 | -12.8 | 36.7 | 3555 | 462
San Diego, CA | Weather_TMY3_SanDiego_CA_722904.txt | 8760 | 16 | 1 | 37 | 1563 | 36
Tucson, AZ | Weather_TMY3_Tucson_AZ_722745.txt | 8760 | 21.7 | -1.1 | 42 | 4803 | 1738

## Hourly_CSV_columns
Column | Unit | Description
City | - | TMY3 location
Hour_of_year | - | 1 to 8760
Hour_start | MM-DD HH:MM | Start of the hour; values are averages over that hour, so kW equals kWh in that hour
T_outdoor_C | C | Outdoor dry-bulb temperature seen by the rooftop condenser
Load_envelope_kW | kW | Heat gain through walls and roof from 20 C store air and through the floor from 10 C ground
Load_product_kW | kW | Heat from incoming product; same daily schedule every day
Load_door_kW | kW | Infiltration of 20 C store air during door openings, 2 min each hour, 08:00-17:00
Load_total_kW | kW | Sum of envelope, product and door loads; identical for all six systems
Cooling_<system>_kW | kW | Cooling delivered by the chiller of that system
Elec_<system>_kW | kW | Chiller electricity of that system; annual sum equals the Annual sheets
Troom_<system>_C | C | Freezer air temperature with that system; setpoint -20 C
<system> | - | SS_R134a, Cascade_R134a_CO2, SS_R1234yf, Cascade_R1234yf_CO2, SS_R515B, Cascade_R515B_CO2; SS = single stage
Files | - | ColdStorage_hourly_21C_condensing_limit.csv and ColdStorage_hourly_No_condensing_limit.csv, 4 cities x 8760 h each