## Slide 1
Symbol | Term and definition | Value used | Source
GWP | Global warming potential: warming from 1 kg of refrigerant relative to 1 kg of CO₂ over 100 years | R-134a 1530 R-1234yf 0.501 R-515B 321.6 R-744 1 | [1], [2]
m | Refrigerant charge in the system (kg) | 2 kg/kW × 60 kW = 120 kg R-744 in cascade: 60 kg | [3]
L | Leak rate: fraction of the charge lost per year | 10 % per year | [4]
n | System lifetime (years) | 15 years | [4]
α | Recovery factor: fraction of the charge recovered at end of life | 70 % | [4]
E | Annual electricity consumption (kWh per year) | Modelica annual results, 4 cities, with and without 21 °C condensing limit | This work
β | Grid emission factor: kg CO₂e emitted per kWh of electricity | Chicago 0.416 Atlanta 0.384 San Diego 0.195 Tucson 0.320 | [5]
Summed over every refrigerant in the system (cascade: hot loop + R-744).

## Slide 2
[1] IPCC, AR6 WGI, Chapter 7 Supplementary Material, Table 7.SM.7 (2021).
[2] ASHRAE Standard 34-2019, Addendum p, Table 4-2 (R-515B composition 91.1 % R-1234ze(E) / 8.9 % R-227ea; GWP mass-weighted).
[3] E. Bellos and C. Tzivanidis, Appl. Sci. 9(4), 790 (2019).
[4] IPCC, 2019 Refinement to the 2006 Guidelines, Vol. 3, Ch. 7, Table 7.9 (medium and large commercial refrigeration).
[5] U.S. EPA, eGRID2023 Summary Tables, rev. 2 (27 March 2025), Table 1.
[6] S. K. Fischer, Int. J. Refrig. 16(6), 423–428 (1993).